## Customer Input
Fixture Count Calculation Form
Project ID (If applicable): | [5 empty] | Date:
Project Name (If applicable): | [6 empty] | (mm/dd/yyyy)
Applicant Name:
Applicant Phone #:
Applicant E-mail Address:
Service Address: | [5 empty] | Unit Type/ Model:
(If multiple building configurations exist)
Please fill in the blue boxes below.
Property Use:
- If multi-family please enter total units
Residual Pressure at Project: |  |  |  | (Please select pressure if known. If unknown leave at 80 psi)
Number of Fixtures
| Fixture or Appliance |  | Public* | Private*
| Toilet (tank) |  |  |  | Common in residential bathrooms
| Toilet (flush valve) |  |  |  | Common in public restrooms
Toilet (flushometer tank)
Bathtub (only)
Bathtub/Shower Combination
Shower (only)
Bathroom Sink (lavatory)
Urinal (tank)
Urinal (3/4" flush valve)
Urinal (1" flush valve)
Bidet
Kitchen Sink
Utility/Service/Mop Sink
Bar Sink
Laundry Sink
Wash-up Sink, each set of faucets
Dishwashing Machine
Washing machine (8 lb.)
Washing machine (15 lb.)
Laundry trays (1 to 3)
Bedpan washers
Drinking fountains
Dental units
Hose Bibb 1/2 in.
Hose Bibb 5/8 in.
Hose Bibb 3/4 in.
Updated June 2018
Calculations based on the AWWA M22 Manual Third Edition, 2015 International Plumbing Code (IPC) and Denver Water Engineering Standards
**IPC Bathroom groups are calculated in the background calculation. Please enter each fixture type above individually.
Definitions
Public vs. Private Utilization:
*Public utilization applies to fixtures in general toilet rooms of schools, gymnasiums, hotels, airports, bus and railroad stations, public buildings, bars,
public comfort stations, office buildings, stadiums, stores, restaurants and other installations where a number of fixtures are installed so that their
utilization is similarly unrestricted.
*Private utilization applies to fixtures in residences and apartments, and to fixtures in nonpublic toilet rooms of hotels and motels and similar
installations in buildings where the plumbing fixtures are intended for utilization by a family or an individual.
**Bathroom Group:
A bathroom group is a defined term as “a group of plumbing fixtures installed in the same room, consisting of one domestic-type lavatory (sink), one water closet (toilet) and either one bathtub (with or without a shower) or one one-head shower.
If any other fixtures (i.e.. Separated bathtub and shower areas), beyond those permitted in circumstances that comply with the definition above, are fed from the piping that leads to a bathroom group, then the fixtures in the bathroom group must be considered individually for determining the fixture unit load.
If a fixture isn't included on this list please type in the fixture name and the
total GPM. This GPM will be added to the final demand after the fixture value/unit
to GPM calculation.

## AWWAvsIPCvsUPC (hidden)
Methodology
| AWWA 04 | AWWA 14 | IPC | UPC
Final Demand (gpm): | #VALUE! | #VALUE! | 1.8638 | 1.8638
Final Meter and Service Size (in): | #VALUE! | #VALUE! | 0.75 | 0.75
Velocity (fps): | #VALUE! | #VALUE! | 1.3542 | 1.3542

## Database (hidden)
Date | Project ID | Project Name | Applicant Name | Applicant Phone | Applicant Email | Service Address | Unit Type | Property Use | Units | Pressure | Bathroom Groups | Toilets (Tanks) | Toilets (Valves) | Toilets (flushometer) | Lavatories | Bathtub/Shower | AWWA04_Demand | AWWA04_Size | AWWA04_Velocity | AWWA14_Demand | AWWA14_Size | AWWA14_Velocity | IPC_Demand | IPC_Size | IPC_Velocity | UPC_Demand | UPC_Size | UPC_Velocity
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.8638 | 0.75 | 1.3542 | 1.8638 | 0.75 | 1.3542

## AWWA_Calculation04 (hidden)
Fixture or Appliance | Fixture Value (at 60 psi) | Number of Fixtures | Subtotal FV
Toilet (tank) | 4 | 0 | 0
Toilet (flush valve) | 35 | 0 | 0
Toilet (flushometer tank) | 4 | 0 | 0
Bathtub (only) | 8 | 0 | 0
Bathtub/Shower Combination | 8 | 0 | 0
Shower (only) | 2.5 | 0 | 0
Bathroom Sink (lavatory) | 1.5 | 0 | 0
Urinal (tank) | 16 | 0 | 0
Urinal (3/4" flush valve) | 35 | 0 | 0
Urinal (1" flush valve) | 35 | 0 | 0
Bidet | 2 | 0 | 0
Kitchen Sink | 2.2 | 0 | 0
Utility/Service/Mop Sink | 4 | 0 | 0
Dishwashing Machine | 2 | 0 | 0
Washing machine (8 lb) | 6 | 0 | 0
Washing machine (15 lb) | 6 | 0 | 0
Laundry trays (1 to 3) | 2.2 | 0 | 0
Bedpan washers | 10 | 0 | 0
Drinking fountains | 2 | 0 | 0
Dental units | 2 | 0 | 0
Hose Bibb 1/2 in. | 5 | 0 | 0
Hose Bibb 5/8 in. | 9 | 0 | 0
Hose Bibb 3/4 in. | 12 | 0 | 0
|  | Total FV: | 0 | Tank - Residential Curve Demand (gpm): | Please enter fixture value
|  |  |  | Valve - Non-Residential Curve Demand (gpm): | This fixture value should be above 25
|  |  |  | Working Pressure (psi): | 0
|  |  |  | Pressure Factor: | #N/A
|  |  |  | Building Use: | 0
|  |  |  | Building Use Code: | Tank
|  |  |  | Number of Units: | 0
Q (cfs) = | #VALUE! |  |  | Final Calculated Demand (gpm): | #VALUE!
A (ft^2) = | #VALUE! |  |  | Calculated Meter and Service Size (In): | #VALUE!
|  |  |  | Final Demand (gpm): | #VALUE!
|  |  |  | Final Meter and Service Size (in): | #VALUE!
|  |  |  | Velocity (fps): | #VALUE!

## AWWA_Calculation14 (hidden)
Fixture or Appliance | Fixture Value (at 60 psi) | Number of Fixtures | Subtotal FV
Toilet (tank) | 6 | 0 | 0
Toilet (flush valve) | 24 | 0 | 0
Toilet (flushometer tank) | 6 | 0 | 0
Bathtub (only) | 8 | 0 | 0
Bathtub/Shower Combination | 8 | 0 | 0
Shower (only) | 2.5 | 0 | 0
Bathroom Sink (lavatory) | 1.5 | 0 | 0
Urinal (tank) | 3 | 0 | 0
Urinal (3/4" flush valve) | 5 | 0 | 0
Urinal (1" flush valve) | 10 | 0 | 0
Bidet | 2 | 0 | 0
Kitchen Sink | 1.8 | 0 | 0
Utility/Service/Mop Sink | 4 | 0 | 0
Dishwashing Machine | 1.3 | 0 | 0
Washing machine (8 lb) | 3 | 0 | 0
Washing machine (15 lb) | 6 | 0 | 0
Laundry trays (1 to 3) | 2.2 | 0 | 0
Bedpan washers | 10 | 0 | 0
Drinking fountains | 2 | 0 | 0
Dental units | 2 | 0 | 0
|  | Total FV: | 0 | Tank - Residential Curve Demand (gpm): | Please enter fixture value
|  |  |  | Valve - Non-Residential Curve Demand (gpm): | This fixture value should be above 25
|  |  |  | Working Pressure (psi): | 0
|  |  |  | Building Use: | 0
|  |  |  | Building Use Code: | Tank
|  |  |  | Number of Units: | 0
|  |  |  | Final Calculated Demand (gpm): | #VALUE!
Q (cfs) = | #VALUE! |  |  | Calculated Meter and Service Size (In): | #VALUE!
A (ft^2) = | #VALUE!
|  | Total Demand (gpm) |  | Final Demand (gpm): | #VALUE!
*Hose Bibb 1/2 in. | 5 | 0 |  | Final Meter and Service Size (in): | #VALUE!
*Hose Bibb 5/8 in. | 9 | 0 |  | Velocity (fps): | #VALUE!
*Hose Bibb 3/4 in. | 12 | 0
*AWWA M22 Manual, Third Edition, page 39
Values do not exist in AWWA

## IPC_Calculation (hidden)
Fixture or Appliance | Public | Private | Number of Public Fixtures | Number of Private Fixtures | Subtotal WSFU
Bathroom Group (tank) |  | 3.6 |  | 0 | 0
Toilet (tank) | 5 | 2.2 | 0 | 0 | 0 |  |  | Bathroom Group Calculation | Entered FV | Final Extra FV
Toilet (flush valve) | 10 | 6 | 0 | 0 | 0 |  |  | Toilet (tank) | 0 | 0
Toilet (flushometer tank) | 2 | 2 | 0 | 0 | 0 |  |  | Bathtub/Shower Combination | 0 | 0
Bathtub/Shower Combination | 4 | 1.4 | 0 | 0 | 0 |  |  | Bathroom Sink (lavatory) | 0 | 0
Bathroom Sink (lavatory) | 2 | 0.7 | 0 | 0 | 0
Urinal (tank) | 3 | 3 | 0 | 0 | 0 |  |  | Bathroom Group Calculation | 0
Urinal (3/4" flush valve) | 5 | 5 | 0 | 0 | 0
Urinal (1" flush valve) | 10 | 10 | 0 | 0 | 0
Bidet |  | 2 | 0 | 0 | 0
Kitchen Sink | 4 | 1.4 | 0 | 0 | 0
Utility/Service/Mop Sink | 3 | 1.4 | 0 | 0 | 0
Dishwashing Machine | 1.4 | 1.4 | 0 | 0 | 0
Washing machine (8 lb.) | 3 | 1.4 | 0 | 0 | 0
Washing machine (15 lb.) | 4 |  | 0 | 0 | 0
Laundry trays (1 to 3) |  | 1.4 | 0 | 0 | 0
Bedpan washers | 4 |  | 0 | 0 | 0
Drinking fountains | 0.25 |  | 0 | 0 | 0
Dental units | 0.25 |  | 0 | 0 | 0
|  |  |  | Total FV: | 0
[6 empty] | Flush Tank Demand (gpm): | 1.8638
[6 empty] | Flush Valve Demand (gpm): | 3
|  | Total Demand (gpm) |  |  |  | Flush Tank or Valve Curve: | Tank
*Hose Bibb 1/2 in. | 5 | 0 |  |  |  | Building Use: | 0
*Hose Bibb 5/8 in. | 9 | 0 |  |  |  | Number of Units: | 0
*Hose Bibb 3/4 in. | 12 | 0
[6 empty] | Final Calculated Demand (gpm): | 1.8638
Q (cfs) = | 0.0041525 |  |  |  |  | Calculated Meter and Service Size (In): | 0.75
A (ft^2) = | 0.0030664
[6 empty] | Final Demand (gpm): | 1.8638
[6 empty] | Final Meter and Service Size (in): | 0.75
[6 empty] | Velocity (fps): | 1.3542
* IPC 2015 Appendix E Section E102.2.2 and Section E103.3
Values do not exist in IPC

## UPC_Calculation (hidden)
Fixture or Appliance | Public | Private | Number of Public Fixtures | Number of Private Fixtures | Subtotal WSFU
Toilet (tank) | 2.5 | 2.5 | 0 | 0 | 0
Toilet (flush valve) | 5 | 5 | 0 | 0 | 0
Toilet (flushometer tank) | 2.5 | 2.5 | 0 | 0 | 0
Bathtub/Shower Combination | 4 | 4 | 0 | 0 | 0
Shower (Only) | 2 | 2 | 0 | 0 | 0
Bathroom Sink (lavatory) | 1 | 1 | 0 | 0 | 0
Urinal (tank) | 2 | 2 | 0 | 0 | 0
Urinal (3/4" flush valve) | 4 | 3 | 0 | 0 | 0
Urinal (1" flush valve) | 5 | 4 | 0 | 0 | 0
Bidet |  | 1 | 0 | 0 | 0
Kitchen Sink | 1.5 | 1.5 | 0 | 0 | 0
Utility/Service/Mop Sink | 3 | 1.5 | 0 | 0 | 0
Bar Sink | 2 | 1 | 0 | 0 | 0
Laundry Sink | 1.5 | 1.5 | 0 | 0 | 0
Wash-up Sink, each set of faucets | 2 |  | 0 | 0 | 0
Dishwashing Machine | 1.5 | 1.5 | 0 | 0 | 0
Washing machine (8 lb.) | 4 | 4 | 0 | 0 | 0
Washing machine (15 lb.) | 4 |  | 0 | 0 | 0
Laundry trays (1 to 3) |  | 1.4 | 0 | 0 | 0
Bedpan washers | 4 |  | 0 | 0 | 0
Drinking fountains | 0.5 |  | 0 | 0 | 0
Dental units | 1 |  | 0 | 0 | 0
Hose Bibb | 2.5 | 2.5 | 0 | 0 | 0
Hose Bibb, each additional | 1 | 1 | 0 | 0 | 0
|  |  |  | Total FV: | 0
[6 empty] | Flush Tank Demand (gpm): | 1.8638
[6 empty] | Flush Valve Demand (gpm): | 3
[6 empty] | Flush Tank or Valve Curve: | Tank
[6 empty] | Building Use: | 0
[6 empty] | Number of Units: | 0
[6 empty] | Final Calculated Demand (gpm): | 1.8638
Q (cfs) = | 0.0041525 |  |  |  |  | Calculated Meter and Service Size (In): | 0.75
A (ft^2) = | 0.0030664
[6 empty] | Final Demand (gpm): | 1.8638
[6 empty] | Final Meter and Service Size (in): | 0.75
[6 empty] | Velocity (fps): | 1.3542
* IPC 2015 Appendix E Section E102.2.2 and Section E103.3
Values do not exist in UPC

## AWWA_Pressure (hidden)
Working Pressure at Meter Discharge (psi) | Pressure Adjustment Factor
35 | 0.74
40 | 0.8
45 | 0.85
50 | 0.9
55 | 0.95
60 | 1
65 | 1.05
70 | 1.09
75 | 1.13
80 | 1.17
85 | 1.21
90 | 1.25
95 | 1.3
100 | 1.34
105 | 1.3895
110 | 1.4345
115 | 1.4795
120 | 1.5245
125 | 1.5695
130 | 1.6145
135 | 1.6595
140 | 1.7045
35 PSI to 100 PSI from AWWA M22 Second Edition
> 100 PSI was extrapolated from slope equation based on trendline of AWWA values

## Domestic_Sizing (hidden)
Maximum Flow (110%) | Tap Size
15.1 | 0.75
26.9 | 1
60.6 | 1.5
107.7 | 2
242.2 | 3
430.6 | 4
968.9 | 6
1722.5 | 8
2691.4 | 10